## Tags
Dimension | Tag | Definition | Related Terminologies | hasSynonym | Author | Reviewed | Review Count | Comments
Equipment>HVAC | HX | Heat Exchanger
Equipment>Fire Safety System | FCP | Fire Control Panel
Equipment>Water System | CWS | Chilled Water System
Equipment>Water System | DHWS | Domestic Hot Water System
Equipment>Water System | HWS | Hot Water System
MeasurementProperty>Modifier | Safety
MeasurementProperty>PhysicalProperties | PIR | Passive Infra Red
MeasurementProperty>PhysicalProperties | Ventilation
Equipment | HVAC
Equipment>Energy>Power | Load |  | Eletrical load |  | Jason
Equipment>Energy>Power | Bus | A metallic strip or bar (typically copper, brass or aluminium) that conducts electricity. Or bus bar. |  |  | Jason
Equipment>Energy>Power | Battery |  |  |  | Jason
Equipment>Energy>Power | Solar |  | Solar panel |  | Jason
Equipment>Energy>Power | PV |  | Abbreviation of Photovoltaic |  | Jason
Equipment>HVAC | AHU
Equipment>HVAC | CRAC
Equipment>HVAC | VFD
Equipment>HVAC | Compressor
Equipment>HVAC | VAV
Equipment>HVAC | FCU
Equipment | Lighting
Equipment>HVAC>AHU | Heating |  | heating coil |  | Jingkun
Equipment>HVAC>AHU | Cooling |  | cooling coil |  | Jingkun
Equipment>HVAC>AHU | Coil |  | heating/cooing coil |  | Jingkun
Equipment>HVAC>AHU | Hot |  | hot water vavle |  | Jingkun
Equipment>HVAC>AHU | Steam |  | steam water valve |  | Jingkun
Equipment>HVAC>AHU | Exhaust |  | Exhaust Fan |  | Jason
Equipment>HVAC>AHU | Return |  | Return Air Temperature |  | Jason
Equipment>HVAC>AHU | Mixed |  | Mixed Air Temperature |  | Jason
Equipment>HVAC>AHU | Chilled |  | Chilled Water Vavle |  | Jingkun
Equipment>HVAC>AHU | Water |  | Chilled Water Vavle |  | Jingkun
Equipment>HVAC>AHU | Outside |  | Outside Air Temperature |  | Jason
Equipment>HVAC>AHU | Bypass |  | Bypass Damper |  | Jason
Equipment>HVAC>AHU | Dehumidification |  |  |  | Jason
Equipment>HVAC>AHU | Humidification |  |  |  | Jason
Equipment>HVAC>AHU | Condensate |  |  |  | Jason
Equipment>HVAC>Misc | Head | Head on a gas tube | High Head Pressure Sensor
Equipment>HVAC>Misc | Computer
Equipment>HVAC>Misc | Humidifier
Equipment>HVAC>VAV | Variable |  | Variable Air Volume Box |  | Jason
Equipment>HVAC>VAV | Air |  | Variable Air Volume Box |  | Jason
Equipment>HVAC>VAV | Volume |  | Variable Air Volume Box |  | Jason
Equipment>HVAC>VAV | Box |  | Variable Air Volume Box |  | Jason
Equipment>HVAC>VAV | Reheat |  | Reheat Valve |  | Jason
Equipment>HVAC>VAV | Discharge |  | Discharge Air Flow Sensor | Supply | Jason
Equipment>HVAC>VAV | Damper |  | Damper Position |  | Jason
Equipment>HVAC>VAV | Position |  | Damper Position |  | Jason
Equipment>HVAC>VAV | Booster |  | Booster Fan |  | Jason
Equipment>HVAC>VAV | Fan |  | Booster Fan |  | Jason
Equipment>HVAC>VAV | Thermostat |  | thermostat |  | Jason
Equipment>HVAC>VAV | Adjustment |  | Delta temperature setpoint (usually from thermostat) |  | Jason
Equipment>HVAC>VAV | Static |  |  |  | Jason
Equipment>HVAC>VAV | Heater |  | Space Heater |  | Jason
Equipment>HVAC>VAV | Mixed
Equipment>HVAC>VFD | Drive |  |  |  | Bharath
Equipment>HVAC>VFD | Speed |  |  |  | Bharath
Equipment>HVAC>VFD | Torque |  |  |  | Bharath
Equipment>HVAC>VFD | Acceleration |  |  |  | Bharath
Equipment>HVAC>VFD | Deceleration |  |  |  | Jason
Equipment>HVAC>VFD | Limit |  |  |  | Bharath
Equipment>HVAC>VFD | Run |  |  |  | Bharath
Equipment>HVAC>VFD | Enable |  |  |  | Bharath
Equipment>HVAC>VFD | Manual |  | Synonym: Hand |  | Bharath
Equipment>HVAC>VFD | Auto |  |  |  | Bharath
Equipment>HVAC>VFD | Direction |  |  |  | Bharath
Equipment>HVAC>VFD | Maintenance |  |  |  | Bharath
Equipment>HVAC>VFD | Required |  |  |  | Bharath
Equipment>HVAC>VFD | Filter |  |  |  | Bharath
Equipment>HVAC>VFD | Panel |  | TagSet: Panel Lockout |  | Bharath
Equipment>HVAC>VFD | Lockout |  |  |  | Bharath
Equipment>HVAC>VFD | Output |  |  |  | Bharath
Equipment>HVAC>VFD | Economizer
Equipment>HVAC>VFD | Reference |  |  |  | Jason
Equipment>HVAC>VFD | Motor |  |  |  | Bharath
Equipment>HVAC>VFD | Rated |  | TagSet: Rated Speed |  | Bharath
Equipment>HVAC>VFD | Dead |  | Dead Band |  | Jason
Equipment>HVAC>VFD | Band |  | Dead Band |  | Jason
Equipment>HVAC>Water | Hot |  | Hot Water Pump |  | Jason
Equipment>HVAC>Water | Medium |  | Medium Temperature Water |  | Jason
Equipment>HVAC>Water | Chilled |  | Chilled Water Pump |  | Jason
Equipment>HVAC>Water | Water |  | Chilled Water Pump, Hot Water Pump |  | Jason
Equipment>HVAC>Water | Pump |  | Chilled Water Pump, Hot Water Pump |  | Jason
Equipment>HVAC>Water | Heat |  | Heat Exchanger |  | Jason
Equipment>HVAC>Water | Exchanger |  | Heat Exchanger |  | Jason
Equipment>HVAC>Water | Valve |  | Heat Exchanger Valve Command |  | Jason
Equipment>HVAC>Water | Stream |  | Steam Pressure Sensor, Stream Flow Sensor |  | Jason
Equipment>HVAC>Water | Differential |  | Chilled Water Differential Pressure Setpoint |  | Jason
Equipment>HVAC>Water | Freeze |  | Freeze Status |  | Jason
Equipment>Lighting | LED
Location | Zone |  | Zone temperature |  | Jason
Location | Room |  |  |  | Jason
Location | Floor |  |  |  | Jason
Location | Building |  |  |  | Jason
Location | Space |  | Space Heater |  | Jason |  |  | (Zone, Room, space, these are confusing. Any suggestion?, Jason)
Location | Wing |  |  |  | Joern
Location | Outside
Location | City
MeasurementProperty>Modifier | Liquid |  | Liquid Detected Alarm |  | Jason
MeasurementProperty>Modifier | Smoke |  |  |  | Jason
MeasurementProperty>Modifier | Domestic |  | Domestic Hot Water Control Valve |  | Jason
MeasurementProperty>Modifier | Zenith |  | Solar Zenith Angle |  | Jason
MeasurementProperty>Modifier | Azimuth |  | Solar Azimuth Angle |  | Jason
MeasurementProperty>Modifier | Request |  |  |  | Jingkun
MeasurementProperty>Modifier | Indicator |  |  |  | Bharath
MeasurementProperty>Modifier | Reset |  |  |  | Bharath
MeasurementProperty>Modifier | PID |  |  |  | Bharath
MeasurementProperty>Modifier | Control |  |  |  | Bharath
MeasurementProperty>Modifier | High |  |  |  | Jason
MeasurementProperty>Modifier | Low |  |  |  | Jason
MeasurementProperty>Modifier | Disable |  |  | off | Jason
MeasurementProperty>Modifier | Enable |  |  | on | Bharath
MeasurementProperty>Modifier | Mode | Operation type | Maintenance mode
MeasurementProperty>Modifier | Start |  |  |  | Bharath
MeasurementProperty>Modifier | Stop |  |  |  | Bharath
MeasurementProperty>Modifier | Max |  |  |  | Jason
MeasurementProperty>Modifier | Min |  |  |  | Jason
MeasurementProperty>Modifier | System |  |  |  | Jason
MeasurementProperty>Modifier | Ready |  |  |  | Jason
MeasurementProperty>Modifier | Emergency |  | Emergency Power Off System |  | Jason
MeasurementProperty>Modifier | Tolerance |  | Humidity Tolerance |  | Jason
MeasurementProperty>Modifier | Delay |  |  |  | Jason
MeasurementProperty>Modifier | Input |  |  |  | Jason
MeasurementProperty>Modifier | Output |  |  |  | Jason
MeasurementProperty>Modifier | Leak |  |  |  | Jason
MeasurementProperty>Modifier | Standby |  |  |  | Jason
MeasurementProperty>Modifier | Conditioning |  | Air Conditioning |  | Jason |  |  | (Jason, Not sure it is necessary, but used in labels.)
MeasurementProperty>Modifier | Overload |  | Fan Overload |  | Jason
MeasurementProperty>Modifier | Detected |  | Smoke Detected Alarm |  | Jason |  |  | (Jason, Not sure it is necessary, but used in labels. Maybe redundant with Alarm.)
MeasurementProperty>Modifier | Communication |  | Communication Status of System |  | Jason
MeasurementProperty>Modifier | Loss |  |  |  | Jason
MeasurementProperty>Modifier | Suction |  |  |  | Jason
MeasurementProperty>Modifier | Relative |  | Relative Humidity |  | Jason
MeasurementProperty>Modifier | Estimation | For a (maybe virtual) point where values are not measured but estimated. |  | Calculation | Jason
MeasurementProperty>Modifier | Capacity |  |  |  | Jason
MeasurementProperty>Modifier | No
MeasurementProperty>Modifier | Wind
MeasurementProperty>Modifier | Auto
MeasurementProperty>Modifier | Storage
MeasurementProperty>Modifier | Activated
MeasurementProperty>Modifier | Hood
MeasurementProperty>Modifier | Yearly
MeasurementProperty>Modifier | Off
MeasurementProperty>Modifier | Generator
MeasurementProperty>Modifier | Cold
MeasurementProperty>Modifier | Underfloor
MeasurementProperty>Modifier | Supply
MeasurementProperty>Modifier | Change
MeasurementProperty>Modifier | Stage
MeasurementProperty>Modifier | Face
MeasurementProperty>Modifier | Radiance
MeasurementProperty>Modifier | Short
MeasurementProperty>Modifier | Deionised
MeasurementProperty>Modifier | When
MeasurementProperty>Modifier | Stack
MeasurementProperty>Modifier | Failed
MeasurementProperty>Modifier | From
MeasurementProperty>Modifier | Push
MeasurementProperty>Modifier | Hold
MeasurementProperty>Modifier | Increase
MeasurementProperty>Modifier | Locally
MeasurementProperty>Modifier | Demand
MeasurementProperty>Modifier | Humidify
MeasurementProperty>Modifier | DualBand
MeasurementProperty>Modifier | Dewpoint
MeasurementProperty>Modifier | Average
MeasurementProperty>Modifier | Thermal
MeasurementProperty>Modifier | Tower
MeasurementProperty>Modifier | Temporary
MeasurementProperty>Modifier | Lead
MeasurementProperty>Modifier | Stages
MeasurementProperty>Modifier | Effective
MeasurementProperty>Modifier | Fire
MeasurementProperty>Modifier | Turned
MeasurementProperty>Modifier | Velocity
MeasurementProperty>Modifier | Meter
MeasurementProperty>Modifier | Grains
MeasurementProperty>Modifier | Shutdown
MeasurementProperty>Modifier | Integration
MeasurementProperty>Modifier | Freezer
MeasurementProperty>Modifier | Lag
MeasurementProperty>Modifier | Percent
MeasurementProperty>Modifier | Fans
MeasurementProperty>Modifier | Highest
MeasurementProperty>Modifier | Conductivity
MeasurementProperty>Modifier | Sash
MeasurementProperty>Modifier | Piezoelectric
MeasurementProperty>Modifier | EconCycle
MeasurementProperty>Modifier | Handler
MeasurementProperty>Modifier | Lowest
MeasurementProperty>Modifier | Cycle
MeasurementProperty>Modifier | Overridden
MeasurementProperty>Modifier | Level
MeasurementProperty>Modifier | Turn
MeasurementProperty>Modifier | Last
MeasurementProperty>Modifier | Month
MeasurementProperty>Modifier | Proportional
MeasurementProperty>Modifier | Shed
MeasurementProperty>Modifier | Monthly
MeasurementProperty>Modifier | Digital
MeasurementProperty>Modifier | Decrease
MeasurementProperty>Modifier | Cooling
MeasurementProperty>Modifier | Integral
MeasurementProperty>Modifier | Short
MeasurementProperty>Modifier | Step
MeasurementProperty>Modifier | Pre
MeasurementProperty>Modifier | Even
MeasurementProperty>Modifier | Detection
MeasurementProperty>Modifier | Peak
MeasurementProperty>Modifier | To
MeasurementProperty>Modifier | Fume
MeasurementProperty>Modifier | Usage
MeasurementProperty>Modifier | Date
MeasurementProperty>Modifier | Today
MeasurementProperty>Modifier | Preheat
MeasurementProperty>Modifier | Alarm
MeasurementProperty>Modifier | Code
MeasurementProperty>Modifier | Cycle
MeasurementProperty>Modifier | Button
MeasurementProperty>Modifier | Analog
MeasurementProperty>Modifier | Open
MeasurementProperty>Modifier | Wheel
MeasurementProperty>Modifier | On
MeasurementProperty>Modifier | Perimeter
MeasurementProperty>Modifier | Remotely
MeasurementProperty>Modifier | Schedule
MeasurementProperty>Modifier | By
MeasurementProperty>Modifier | Environment
MeasurementProperty>Modifier | Enthalpy
MeasurementProperty>Modifier | Glycool
MeasurementProperty>Modifier | Current
MeasurementProperty>PhysicalProperties | Time |  |  |  | Bharath
MeasurementProperty>PhysicalProperties | Voltage |  |  |  | Bharath
MeasurementProperty>PhysicalProperties | Power |  |  |  | Bharath
MeasurementProperty>PhysicalProperties | Current | Alternating Current - usually used for power measurements |  |  | Bharath |  |  | (Is this electric current?, Jason)
MeasurementProperty>PhysicalProperties | Energy |  |  |  | Bharath
MeasurementProperty>PhysicalProperties | DC | Direct Current - usually used for digital control |  |  | Bharath
MeasurementProperty>PhysicalProperties | Temperature |  |  |  | Jason
MeasurementProperty>PhysicalProperties | Flow | Fluidic stream | Discharge Air Flow Sensor |  | Jason
MeasurementProperty>PhysicalProperties | Pressure |  |  |  | Jason
MeasurementProperty>PhysicalProperties | Humidity |  |  |  | Jason
MeasurementProperty>PhysicalProperties | Enthalpy |  |  |  | Jason
MeasurementProperty>PhysicalProperties | Angle |  | Solar Zenith Angle |  | Jason
MeasurementProperty>PhysicalProperties | Fault |  |  |  | Bharath
MeasurementProperty>PhysicalProperties | Switch | Physical switch | Light switch, Emergency Power Off Switch |  | Jason
MeasurementProperty>PhysicalProperties | Status |  |  |  | Bharath
MeasurementProperty>PhysicalProperties | Alarm |  |  |  | Bharath
MeasurementProperty>PhysicalProperties | CO2 |  | CO2 Sensor |  | Jason
MeasurementProperty>PhysicalProperties | Occupancy |  |  |  | Jsaon
MeasurementProperty>PhysicalProperties | Occupied | Indicates something is occupied. |  |  | Jsaon
MeasurementProperty>PhysicalProperties | Unoccupied |  |  |  | Jason
MeasurementProperty>PhysicalProperties | Frequency |  |  |  | Bharath
MeasurementProperty>PhysicalProperties | Luminance
MeasurementProperty>Unit | Fahrenheit |  |  |  | Jason
MeasurementProperty>Unit | CFM | Cubic feet per minute |  |  | Jason
Point | Setpoint |  |  |  | Bharath
Point | Sensor |  |  |  | Jason |  |  | (Snonym to Level?, Jason)
Point | Status
Point | Command |  |  |  | Bharath
Point | Alarm
Point | Meter
MeasurementProperty>Modifier | Unit
MeasurementProperty>Modifier | Grains
Equipment>Energy>SolarPanel | Photovoltaic
Equipment>HVAC | Terminal
Location | Laboratory
MeasurementProperty>Modifier | Adjust
MeasurementProperty>PhysicalProperties | Rain
MeasurementProperty>PhysicalProperties | Hail
MeasurementProperty>Modifier | Running
MeasurementProperty>Modifier | Warmest
MeasurementProperty>Modifier | Hand
MeasurementProperty>Modifier | Cool
MeasurementProperty>Modifier | Coldest
MeasurementProperty>Modifier | Hour
MeasurementProperty>Modifier | Warm
MeasurementProperty>Modifier | DI
MeasurementProperty>Modifier | Trace
MeasurementProperty>PhysicalProperties | Frost
MeasurementProperty>Modifier | Automatic
MeasurementProperty>Modifier | Duration

## TagSets
Dimension | TagSet | isPointOf | isPartOf | hasSynonym | Definition | hasUnit | hasAbbreviation | can be named? (can be instantiated?) | can be unnamed? (cannot be instantiated?) | Author | Reviewed | Review Count | Discussion
Equipment | Fire Safety System
Equipment | Solar Panel
Equipment | Lighting System
Equipment>Fire Safety System | Fire Control Panel |  |  | FCP |  |  | FCP |  |  | Bharath
Equipment | Heating Ventilation Air Conditioning System |  |  | HVAC
Equipment>HVAC | Space Heater | [6 empty] | O | X | Jason
Equipment>HVAC | Air Handler Unit |  |  | AHU | A device used to regulate and circulate air as part of a heating, ventilating, and air-conditioning (HVAC) system (from Wikipedia) |  | AHU | O | X | Joern
Equipment>HVAC | Computer Room Air Conditioning |  |  | CRAC |  |  | CRAC |  |  | Bharath
Equipment>HVAC | Terminal Unit | [8 empty] | Bharath
Equipment>HVAC | Coil
Equipment>HVAC>Coil | Cooling Coil
Equipment>HVAC>Coil | Heat Exchanger |  |  | HX |  |  | HX |  |  | Bharath
Equipment>HVAC>Coil | Heating Coil |  |  |  | A coil which used to heat supplied air. Can be in both AHU and terminal units |  |  | O | X | Bharath
Equipment>HVAC | Variable Frequency Drive |  |  | VFD | System that controls chilled water used to cool a building's air and equipment |  | VFD | O | X | Bharath
Equipment>HVAC | Valve | [8 empty] | Bharath
Equipment>HVAC>Valve | Chilled Water Valve | [8 empty] | Jason
Equipment>HVAC>Valve | Heating Valve
Equipment>HVAC>Valve | Cooling Valve
Equipment>HVAC>AHU | Exhaust Air Damper | [8 empty] | Josh
Equipment>HVAC>AHU | Heat Wheel VFD |  |  |  | Motor for Heat Wheel |  |  |  |  | Josh
Equipment>HVAC>AHU | Mixed Air Filter | [8 empty] | Jason
Equipment>HVAC>AHU | Preheat Hot Water Valve | [8 empty] | Jason
Equipment>HVAC>AHU | Preheat Valve VFD |  |  |  | Motor for Preheat Valve |  |  |  |  | Josh
Equipment>HVAC>CRAC | Emergency Power Off System | [8 empty] | Bharath
Equipment>HVAC>CWS | Cooling Coil |  |  |  | Equipment to cool air using cold water |  |  | O | X | Jason
Equipment>HVAC>CWS | Cooling Tower | [6 empty] | O | X | Jason
Equipment>HVAC>CWS | Cooling Tower Fan | [6 empty] | O | X | Jason
Equipment>HVAC>Terminal Unit | Fan Coil Unit |  |  | FCU |  |  | FCU |  |  | Josh
Equipment>HVAC>Terminal Unit | Variable Air Volume |  |  | VAV | A type of heating, ventilating, and/or air-conditioning (HVAC) system. VAV systems vary the airflow at a constant temperature. (from Wikipedia) |  | VAV | O | X | Jason
Equipment>HVAC>Fan>Supply Fan | Booster Fan |  |  |  | Supply Fan for VAV |  |  | O | X | Jason
Equipment>HVAC | Fan
Equipment>HVAC>Fan | Supply Fan
Equipment>HVAC>Fan | Return Fan
Equipment>HVAC>Fan | Exhaust Fan
Equipment>HVAC | Pump
Equipment>HVAC>Pump | Hot Water Pump
Equipment>HVAC>Pump | Chilled Water Pump
Equipment>Water System | Chilled Water System |  |  | CWS |  |  |  | O | X | Jason
Equipment>Water System | Hot Water System |  |  | HWS
Equipment>Water System | Domestic Hot Water System |  |  | DHWS
Location | Building
Location | Floor
Location | HVAC Zone
Location | Lighting Zone | [8 empty] | Gabe
Location | Room | [11 empty] | (A TagSet with single Tag, Jason)
Location>Room | Laboratory
Location>Room>Laboratory | Cold Box |  |  |  | A room maintained at cold temperature for storing specimens and chemicals |  |  |  |  | Bharath
Location>Room>Laboratory | Environment Box |  |  |  | Special temperature room for labs |  |  |  |  | Bharath
Location>Room>Laboratory | Freezer |  |  |  | Freezer rooms |  |  |  |  | Bharath
Location>Room>Laboratory | Hot Box |  |  |  | Room maintained at high temperature for labs |  |  |  |  | Bharath
MeasurementProperty>Voltage | Battery Voltage |  | Solar Panel | [6 empty] | Bharath
MeasurementProperty>Current | Photovoltaic Current Output |  | Solar Panel | PV System Output, PV Current Output | [5 empty] | Bharath
MeasurementProperty>Angle | Solar Azimuth Angle |  | Solar Panel | [6 empty] | Bharath
MeasurementProperty>Angle | Solar Zenith Angle |  | Solar Panel | [6 empty] | Bharath
MeasurementProperty>Temperature | Discharge Air Temperature |  | AHU | Supply Air Temperature | [5 empty] | Jason |  |  | Supply Air Temperature
MeasurementProperty>Flow>Air Flow | Fan Air Flow |  | AHU | [6 empty] | Jason
MeasurementProperty>Pressure>Differential Pressure | Filter Differential Pressure |  | AHU | [6 empty] | Bharath
MeasurementProperty>Pressure>Differential Pressure | Heat Wheel Differential Pressure |  | AHU | [6 empty] | Josh
MeasurementProperty>Speed | Heat Wheel Speed |  | AHU | [6 empty] | Josh
MeasurementProperty>Temperature>Discharge Air Temperature | Heat Wheel Discharge Air Temperature |  | AHU | Heat Wheel Supply Air Temperature | [5 empty] | Josh
MeasurementProperty>Voltage | Heat Wheel Voltage |  | AHU | [6 empty] | Josh
MeasurementProperty>CO2 | Outside Air CO2 |  | AHU | [6 empty] | Jason
MeasurementProperty>Dewpoint | Outside Air Dewpoint |  | AHU | [6 empty] | Josh
MeasurementProperty>Enthalpy | Outside Air Enthalpy |  | AHU | [6 empty] | Josh
MeasurementProperty>Flow>Air Flow | Outside Air Flow |  | AHU | [6 empty] | Jason
MeasurementProperty>Grains | Outside Air Grains |  | AHU | [6 empty] | Josh
MeasurementProperty>Humidity | Outside Air Humidity |  | AHU | [6 empty] | Josh
MeasurementProperty>Temperature | Outside Air Temperature |  | AHU |  | @ inlet of the AHU |  |  |  |  | Marco
MeasurementProperty>Temperature>Discharge Air Temperature | Preheat Discharge Air Temperature |  | AHU | Preheat Supply Air Temperature | [5 empty] | Josh
MeasurementProperty>CO2 | Return Air CO2 |  | AHU | [6 empty] | Josh
MeasurementProperty>Dewpoint | Return Air Dewpoint |  | AHU | [6 empty] | Josh
MeasurementProperty>Enthalpy | Return Air Enthalpy |  | AHU | [6 empty] | Josh
MeasurementProperty>Flow>Air Flow | Return Air Flow |  | AHU | [6 empty] | Jason
MeasurementProperty>Grains | Return Air Grains |  | AHU |  | Number of Grains of Water Per Pound of Air. Calculated as a function of temperature and humidity. |  |  |  |  | Josh
MeasurementProperty>Humidity | Return Air Humidity |  | AHU
MeasurementProperty>Flow>Air Flow>Return Air Flow | Return Fan Air Flow |  | AHU |  | Air flow measurements specific to a fan |  |  |  |  | Bharath
MeasurementProperty>Pressure | Static Pressure |  | AHU |  | Static Pressure in the supply duct |  |  |  |  | Marco
MeasurementProperty>Flow>Air Flow>Discharge Air Flow | Supply Fan Air Flow |  | AHU | [6 empty] | Bharath
MeasurementProperty>Piezoelectric | Supply Fan Piezoelectric |  | AHU
MeasurementProperty>Temperature | CRAC Temperature |  | CRAC | [6 empty] | Jason
MeasurementProperty>Flow>Air Flow | Exhaust Air Flow |  | Exhaust System | [6 empty] | Jason
MeasurementProperty>Flow>Air Flow>Exhaust Air Flow | Exhaust Air Stack Flow |  | Exhaust System | [6 empty] | Bharath
MeasurementProperty>Temperature | Exhaust Air Temperature |  | Exhaust System | [6 empty] | Jason
MeasurementProperty>Pressure>Velocity Pressure | Exhaust Air Velocity Pressure |  | Exhaust System | [6 empty] | Bharath
MeasurementProperty>Piezoelectric | Exhaust Fan Piezoelectric |  | Exhaust System |  | Piezoelectric meter of Exhaust Fan |  |  |  |  | Josh
MeasurementProperty>Flow>Air Flow | Booster Fan Air Flow |  | VAV
MeasurementProperty>Position | Damper Position |  | VAV |  |  |  |  | O | X | Jason
MeasurementProperty>Flow>Air Flow | Discharge Air Flow |  | VAV | Supply Air Flow
MeasurementProperty>Pressure>Velocity Pressure | Discharge Air Velocity Pressure |  | VAV | Supply Air Velocity Pressure | [5 empty] | Bharath
MeasurementProperty>Temperature | Room Temperature |  | VAV
MeasurementProperty>Temperature | Zone Temperature |  | VAV |  | Temperature sensor in the thermostat to measure the actual zone temperature
MeasurementProperty>Voltage | DC Bus Voltage |  | VFD |  | Voltage measured on the communication/control lines |  |  | O | X | Bharath
MeasurementProperty>Temperature | Drive Temperature |  | VFD |  | Measures VFD temperature |  |  | O | X | Bharath
MeasurementProperty | Energy |  | VFD |  |  |  |  | O | X | Bharath
MeasurementProperty>Current | Motor Current |  | VFD | Load Current | Measured current |  |  | O | X | Bharath
MeasurementProperty>Power | Motor Power |  | VFD | [6 empty] | Bharath
MeasurementProperty>Speed | Motor Speed |  | VFD | [6 empty] | Jason
MeasurementProperty>Torque | Motor Torque |  | VFD |  | Measured torque |  |  | O | X | Bharath
MeasurementProperty>Frequency | Output Frequency |  | VFD | [6 empty] | Bharath
MeasurementProperty>Voltage | Output Voltage |  | VFD | VFD Voltage | [5 empty] | Bharath
MeasurementProperty>Time | Run Time |  | VFD | Running Hour
MeasurementProperty>Temperature | Cold Box Temperature |  | Laboratory | [6 empty] | Bharath
MeasurementProperty>Temperature | Environment Box Temperature |  | Laboratory | [6 empty] | Bharath
MeasurementProperty>Temperature | Freezer Temperature |  | Laboratory | [6 empty] | Bharath
MeasurementProperty>Temperature | Hot Box Temperature |  | Laboratory | [6 empty] | Bharath
MeasurementProperty>Energy | Thermal Energy |  | Thermal Energy Storage | [6 empty] | Jason
MeasurementProperty>Pressure>Differential Pressure | Chilled Water Differential Pressure |  | Water System | [6 empty] | Jason
MeasurementProperty>Temperature | Chilled Water Discharge Temperature |  | Water System | Chilled Water Supply Temperature | [5 empty] | Jason
MeasurementProperty>Temperature | Chilled Water Return Temperature |  | Water System |  |  |  |  | O | X | Jason
MeasurementProperty>Flow>Water Flow | Chilled Water Supply Flow |  | Water System | [6 empty] | Bharath
MeasurementProperty>Temperature>Differential Temperature | Chilled Water Supply Return Differential Temperature |  | Water System |  | Difference between supply and return temperature |  |  |  |  | Bharath
MeasurementProperty>Conductivity | Deionised Water Conductivity |  | Water System | [6 empty] | Bharath
MeasurementProperty>Temperature | Domestic Hot Water Supply Temperature |  | Water System | [6 empty] | Bharath
MeasurementProperty>Temperature | Heat Exchanger Supply Water Temperature |  | Water System | [6 empty] | Bharath
MeasurementProperty>Temperature>Hot Water Return Temperature | High Temperature Hot Water Return Temperature |  | Water System
MeasurementProperty>Temperature>Hot Water Supply Temperature | High Temperature Hot Water Supply Temperature |  | Water System
MeasurementProperty>Pressure>Differential Pressure | Hot Water Differential Pressure |  | Water System | [6 empty] | Jason
MeasurementProperty>Temperature | Hot Water Supply Temperature |  | Water System | [6 empty] | Jason
MeasurementProperty>Temperature | Hot Water Return Temperature |  | Water System | [6 empty] | Jason
MeasurementProperty>Temperature>Hot Water Return Temperature | Medium Temperature Hot Water Return Temperature |  | Water System | [6 empty] | Jason
MeasurementProperty>Temperature>Hot Water Supply Temperature | Medium Temperature Hot Water Supply Temperature |  | Water System | [6 empty] | Jason
MeasurementProperty>Pressure>Differential Pressure>Hot Water Differential Pressure | Medium Temperature Hot Water Differential Pressure |  | Water System
MeasurementProperty>Temperature | Water Supply Temperature |  | Water System | [6 empty] | Jason
MeasurementProperty>Enthalpy | Outside Enthalpy |  | Weather | [6 empty] | Bharath
MeasurementProperty>Humidity | Relative Humidity |  | Weather | [6 empty] | Bharath
MeasurementProperty | Solar Radiance |  | Weather | [6 empty] | Jason
MeasurementProperty>Direction | Wind Direction |  | Weather | [6 empty] | Jason
MeasurementProperty>Speed | Wind Speed |  | Weather | [6 empty] | Jason
Point>Alarm | Emergency Generator Alarm | Emergency Generator | [7 empty] | Bharath
Point>Alarm | Fume Hood Alarm | Fume Hood | [7 empty] | Bharath
Point>Alarm | CO2 High Alarm | AHU
Point>Alarm | Change Filter Alarm | AHU |  |  | Alarm to change dirty filter |  |  |  |  | Bharath
Point>Alarm | Condensate Leak Alarm | AHU | [7 empty] | Jason
Point>Alarm | Discharge Air Smoke Detected Alarm | AHU | [7 empty] | Bharath
Point>Alarm | Discharge Air Temperature High Limit Alarm | AHU |  | Supply Air Temperature High Limit Alarm
Point>Alarm | Return Air Temperature High Limit Alarm | AHU | [7 empty] | Bharath
Point>Alarm | Compressor Overload Alarm | CRAC | [7 empty] | Bharath
Point>Alarm | Air Flow Loss Alarm | CRAC | [7 empty] | Bharath
Point>Setpoint | Alarm Delay Setpoint | CRAC | [7 empty] | Bharath
Point>Alarm | Communication Loss Alarm | CRAC | [7 empty] | Bharath
Point>Alarm | Condensate Leak Alarm | CRAC | [7 empty] | Bharath
Point>Alarm | Emergency Power Loss Alarm | CRAC | [7 empty] | Bharath
Point>Alarm | Fan Overload Alarm | CRAC | [7 empty] | Bharath |  |  | Also part of CRAC
Point>Alarm | High Head Pressure Alarm | CRAC | [7 empty] | Jason
Point>Alarm | High Humidity Alarm | CRAC | [7 empty] | Bharath
Point>Setpoint | High Humidity Alarm Setpoint | CRAC | [7 empty] | Bharath
Point>Alarm | High Temperature Alarm | CRAC | [7 empty] | Bharath
Point>Setpoint | High Temperature Alarm Setpoint | CRAC | [7 empty] | Bharath
Point>Alarm | Humidifier Alarm | CRAC | [7 empty] | Bharath
Point>Alarm | Humidifier Panel No Water Alarm | CRAC | [7 empty] | Bharath
Point>Alarm | Liquid Detected Alarm | CRAC | [7 empty] | Bharath
Point>Alarm | Low Humidity Alarm | CRAC | [7 empty] | Bharath
Point>Setpoint | Low Humidity Alarm Setpoint | CRAC | [7 empty] | Bharath
Point>Alarm | Low Suction Pressure Alarm | CRAC | [7 empty] | Bharath
Point>Alarm | Low Temperature Alarm | CRAC | [7 empty] | Bharath
Point>Setpoint | Low Temperature Alarm Setpoint | CRAC | [7 empty] | Bharath
Point>Alarm | Power Loss Alarm | CRAC | [7 empty] | Bharath
Point>Alarm | Short Cycle Alarm | CRAC | [7 empty] | Bharath
Point>Alarm | Smoke Detected Alarm | CRAC | [7 empty] | Bharath
Point>Alarm | Unit Failed Alarm | CRAC | [7 empty] | Bharath
Point>Alarm | Water Loss Alarm | CRAC | [7 empty] | Bharath
Point>Alarm | Hot Water Pump Alarm | HWS
Point>Alarm | Maintenance Required Alarm | VFD | [7 empty] | Bharath
Point>Alarm | VFD Alarm | VFD | [7 empty] | Bharath
Point>Alarm | Luminance Alarm | Lighting System
Point>Alarm | Alarm Delay Setpoint | Water System | [7 empty] | Bharath
Point>Alarm | Deionised Water Alarm | Water System |  | DI Water Alarm | [5 empty] | Bharath
Point>Alarm | Pump Alarm | Pump
Point>Command | Start Stop Command
Point>Command | Load Shed Command | Demand Response | [7 empty] | Bharath
Point>Command>Load Shed Command | Standby Load Shed Command | Demand Response |  | Standby Load Shed Switch | [5 empty] | Bharath
Point>Command>Load Shed Command | Unoccupied Load Shed Command | Demand Response |  | Unoccupied Load Shed Switch | [5 empty] | Bharath
Point>Command>Load Shed Command>Standby Load Shed Command | Zone Standby Load Shed Command | Demand Response | [7 empty] | Bharath
Point>Command>Load Shed Command>Unoccupied Load Shed Command | Zone Unoccupied Load Shed Command | Demand Response | [7 empty] | Bharath
Point>Command | Enable Command | HVAC
Point>Command>Cooling Command | Highest Zone Cooling Command | HVAC
Point>Command>Fire Control Panel Off Command | AHU Fire Control Panel Off Command | AHU | [7 empty] | Bharath
Point>Command>Fire Control Panel On Command | AHU Fire Control Panel On Command | AHU | [7 empty] | Bharath
Point>Command>Enable Command | AHU System Enable Command | AHU | [7 empty] | Bharath
Point>Command>Damper Command | Economizer Damper Command | AHU | [7 empty] | Jason |  |  | (Maybe synonymous to Economizer Mode?, Jason)
Point>Command>Damper Command | Mixed Air Damper Position Command | AHU | [7 empty] | Josh
Point>Command>Damper Command | Outside Air Damper Position Command | AHU | [7 empty] | Josh
Point>Command>Valve Command | Return Air Preheat Valve Command | AHU | [7 empty] | Josh
Point>Command>Start Stop Command | Return Fan Start Stop Command | AHU |  | Return Fan Command | [5 empty] | Jason
Point>Command>Request Command | Run Request Command | AHU |  |  | Request to have AHU turn on |  |  |  |  | Josh
Point>Command>Start Stop Command | Supply Fan Start Stop Command | AHU |  | Supply Fan Command | [5 empty] | Jason
Point>Command>Shutdown Command | System Shutdown Command | AHU | [7 empty] | Bharath
Point>Command>Speed Command>VFD Speed Command | Supply Fan VFD Command | AHU |  |  | AHU commands its supply fans to run at specified % of its capacity
Point>Command>Speed Command>VFD Speed Command | Return Fan VFD Command | AHU |  |  | AHU commands its return fans to run at specified % of its capacity
Point>Command>Mode Command | Automatic Mode Command | AHU
Point>Command>Valve Command | Return Heat Valve Command | AHU
Point>Command>Start Stop Command | CRAC Pump Start Stop Command | CRAC | [7 empty] | Bharath
Point>Command | Emergency Power Off Command | CRAC |  | Emergency Power Off Switch Command | [5 empty] | Bharath
Point>Command | Humidify Command | CRAC | [7 empty] | Josh
Point>Command>Start Stop Command | Unit Start Stop Command | CRAC |  | Unit Run Command | [5 empty] | Bharath
Point>Command>Speed Command>VFD Speed Command | Chilled Water Pump VFD Command | CWS
Point>Command>Valve Command | Chilled Water Bypass Valve Command | CWS | [7 empty] | Bharath
Point>Command>Enable Command | Chilled Water System Enable Command | CWS | [5 empty] | O |  | Jason
Point>Command>Start Stop Command | Chilled Water Pump Start Stop Command | CWS |  | Chilled Water Pump Command | [5 empty] | Jason
Point>Command>Pump Lead Lag Command | Chilled Water Pump Lead Lag Command | CWS
Point>Command>Fans Stage Command | Building Exhaust Fans Stage Command | Exhaust System |  |  | Exhaust fans are typically arranged so that they can be fired in stages as per requirement. This command controls which stage is switched on |  |  |  |  | Bharath
Point>Command>Damper Command | Exhaust Bypass Damper Command | Exhaust System | [7 empty] | Bharath
Point>Command>Enable Command | Exhaust Fan Enable Command | Exhaust System |  |  | Enable switch for one particular exhaust fan |  |  |  |  | Bharath
Point>Command>Fire Control Panel Off Command | Exhaust Fan Fire Control Panel Off Command | Exhaust System | [7 empty] | Bharath
Point>Command>Fire Control Panel On Command | Exhaust Fan Fire Control Panel On Command | Exhaust System | [7 empty] | Bharath
Point>Command>Start Stop Command | Exhaust Fan Start Stop Command | Exhaust System |  | Exhaust Fan Command | [5 empty] | Bharath
Point>Command>Enable Command | Exhaust Fan System Enable Command | Exhaust System |  |  | Enable switch for a collection of exhaust fans |  |  |  |  | Bharath
Point>Command>Speed Command>VFD Speed Command | Hot Water Pump VFD Command | HWS
Point>Command>Enable Command | Hot Water System Enable Command | HWS | [7 empty] | Jason
Point>Command>Shutdown Command | Shutdown Hot Water When Unoccupied Command | HWS | [7 empty] | Bharath
Point>Command>Valve Command | Heat Exchanger Valve Command | HWS | [7 empty] | Bharath
Point>Command>Pump Lead Lag Command | Hot Water Pump Lead Lag Command | HWS
Point>Command>Start Stop Command | Hot Water Pump Start Stop Command | HWS | [7 empty] | Jason
Point>Command>Start Stop Command | Booster Fan Start Stop Command | VAV |  | Booster Fan Command |  |  |  | O | X | Jason
Point>Command | Cooling Command | VAV | [5 empty] | O | X | Jason
Point>Command | Damper Command | VAV | [5 empty] | O | X | Jason
Point>Command | Discharge Air Flow Command | VAV | [7 empty] | Josh
Point>Command | Heating Command | VAV | [5 empty] | O | X | Jason
Point>Command>Valve Command | Heating Valve Command | VAV | [5 empty] | O | X | Jason
Point>Command | Occupancy Command | VAV |  | Occupied Command |  |  |  | O | X | Jason
Point>Command>Valve Command | Reheat Valve Command | VAV | [5 empty] | O | X | Jason
Point>Command>Mode Command | VAV Box Mode Command | VAV | [7 empty] | Bharath
Point>Command>Valve Command | Cooling Valve Command | VFD |  |  | Can also be part of CRAC |  |  | O | X | Jason
Point>Command>Reset Command | Fault Reset Command | VFD |  |  | Command to reset fault status after fixed by operator |  |  |  |  | Bharath
Point>Command>Reset Command | Filter Reset Command | VFD |  |  | Command to reset the filter status |  |  | O | X | Bharath
Point>Command | Frequency Command | VFD | [7 empty] | Bharath
Point>Command>Mode Command | Maintenance Mode Command | VFD | [7 empty] | Jason
Point>Command>Frequency Command | Max Frequency Command | VFD | [7 empty] | Bharath
Point>Command | Panel Lockout Command | VFD | [5 empty] | O | X | Bharath
Point>Command>Direction Command | Run Direction Command | VFD |  | Motor Direction Command | Command to change VFD direction |  |  | O | X | Bharath
Point>Command>Enable Command | Run Enable Command | VFD |  | VFD Run Enable,Run Enable Command | A command that allows VFD to be used |  |  | O | X | Bharath
Point>Command>Speed Command | VFD Speed Command | VFD |  | VFD Command | Tells the VFD to run at certain % of its capacity |  |  |  |  | Bharath
Point>Command>Enable Command | VFD System Enable Command | VFD |  |  | A group of VFDs being enabled or disabled |  |  |  |  | Bharath
Point>Command>Start Stop Command | VFD Start Stop Command | VFD |  | Motor Start Stop Command | Command to turn on/off VFD |  |  | O | X | Bharath
Point>Command | Luminance Command | Lighting System
Point>Command>Valve Command | Perimeter Heating Valve Command | Water System | [7 empty] | Josh
Point>Command | Valve Command | Water System
Point>Command>Enable Command | Domestic Hot Water System Enable Command | DomesticHWS | [7 empty] | Bharath
Point>Command>Start Stop Command | Domestic Hot Water System Start Stop Command | DomesticHWS | [7 empty] | Bharath
Point>Command>Valve Command | Domestic Hot Water Valve Command | DomesticHWS | [7 empty] | Bharath
Point>Command | Pump Lead Lag Command | Pump |  | Pump Lead On Off
Point>Command>Start Stop Command | Pump Start Stop Command | Pump | [7 empty] | Jason
Point>Setpoint>Capacity Setpoint | CRAC Capacity Setpoint | CRAC | [7 empty] | Josh
Point>Setpoint | Humidity Setpoint | CRAC | [7 empty] | Bharath
Point>Setpoint>Tolerance Setpoint | Humidity Tolerance Setpoint | CRAC | [7 empty] | Jason
Point>Setpoint | Temperature Setpoint | CRAC | [7 empty] | Bharath
Point>Setpoint>Tolerance Setpoint | Temperature Tolerance Setpoint | CRAC | [7 empty] | Bharath
Point>Meter | Power Meter | Power | [7 empty] | Jason
Point>Meter>Flow Meter | Hot Water Flow Meter | HWS
Point>Meter>Steam Usage Meter | Current Steam Usage Meter | Steam | [7 empty] | Josh
Point>Meter>Steam Usage Meter | Monthly Steam Usage Meter | Steam | [7 empty] | Josh
Point>Meter>Energy Meter | Peak Energy Today Meter | Steam | [7 empty] | Josh
Point>Meter>Steam Usage Meter | Steam Usage Today Meter | Steam | [7 empty] | Josh
Point>Meter>Steam Usage Meter | Yearly Steam Usage Meter | Steam | [7 empty] | Josh
Point>Meter | Water Meter | Water System
Point>Meter>Water Meter | Hot Water Meter | HWS
Point>Sensor>Voltage Sensor | Battery Voltage Sensor | Solar Panel | [7 empty] | Bharath
Point>Sensor>Current Sensor | Photovoltaic Current Output Sensor | Solar Panel |  | PV System Output Sensor, PV Current Output Sensor | [5 empty] | Bharath
Point>Sensor>Angle Sensor | Solar Azimuth Angle Sensor | Solar Panel | [7 empty] | Bharath
Point>Sensor>Angle Sensor | Solar Zenith Angle Sensor | Solar Panel | [7 empty] | Bharath
Point>Sensor>Flow Sensor>Air Flow Sensor | Fume Hood Air Flow Sensor | Fume Hood | [7 empty] | Bharath
Point>Sensor>Damper Position Sensor | Fume Hood Sash Position Sensor | Fume Hood | [7 empty] | Bharath
Point>Sensor | Average Cooling Demand Sensor | HVAC |  |  | Average of cooling demand across thermal zones. This could be for one AHU or one floor or entire building |  |  |  |  | Bharath
Point>Sensor>Flow Sensor>Air Flow Sensor>Discharge Air Flow Sensor | Average Discharge Air Flow Sensor | HVAC |  | Average Supply Air Flow Sensor | Average of supply air to thermal zones. Granurality: AHU, floor, building |  |  |  |  | Bharath
Point>Sensor>Temperature Sensor>Zone Temperature Sensor | Average Zone Temperature Sensor | HVAC | [7 empty] | Bharath
Point>Sensor>Temperature Sensor>Zone Temperature Sensor | Highest Zone Temperature Sensor | HVAC |  | Warmest Zone Temperature Sensor | [5 empty] | Bharath
Point>Sensor>Temperature Sensor>Zone Temperature Sensor | Lowest Zone Temperature Sensor | HVAC |  | Coldest Zone Temperature Sensor | [5 empty] | Bharath
Point>Sensor>Temperature Sensor | Discharge Air Temperature Sensor | AHU |  | Supply Air Temperature Sensor | [5 empty] | Jason |  |  | Supply Air Temperature
Point>Sensor>Dewpoint Sensor | Outside Air Dewpoint Sensor | AHU | [7 empty] | Josh
Point>Sensor>Enthalpy Sensor | Outside Air Enthalpy Sensor | AHU | [7 empty] | Josh
Point>Sensor>Flow Sensor>Air Flow Sensor | Outside Air Flow Sensor | AHU | [7 empty] | Jason
Point>Sensor>Air Grains Sensor | Outside Air Grains Sensor | AHU | [7 empty] | Josh
Point>Sensor>Humidity Sensor | Outside Air Humidity Sensor | AHU | [7 empty] | Josh
Point>Sensor>Temperature Sensor | Outside Air Temperature Sensor | AHU |  |  | @ inlet of the AHU |  |  |  |  | Marco
Point>Sensor>Temperature Sensor>Discharge Air Temperature Sensor | Preheat Discharge Air Temperature Sensor | AHU |  | Preheat Supply Air Temperature Sensor | [5 empty] | Josh
Point>Sensor>CO2 Sensor | Return Air CO2 Sensor | AHU | [7 empty] | Josh
Point>Sensor>Dewpoint Sensor | Return Air Dewpoint Sensor | AHU | [7 empty] | Josh
Point>Sensor>Enthalpy Sensor | Return Air Enthalpy Sensor | AHU | [7 empty] | Josh
Point>Sensor>Flow Sensor>Air Flow Sensor | Return Air Flow Sensor | AHU | [7 empty] | Jason
Point>Sensor>Air Grains Sensor | Return Air Grains Sensor | AHU | [7 empty] | Josh
Point>Sensor>Humidity Sensor | Return Air Humidity Sensor | AHU
Point>Sensor>Flow Sensor>Air Flow Sensor>Fan Air Flow Sensor | Return Fan Air Flow Sensor | AHU |  |  | Air flow measurements specific to a fan |  |  |  |  | Bharath
Point>Sensor>Pressure Sensor | Static Pressure Sensor | AHU |  |  | Static Pressure in the supply duct |  |  |  |  | Marco
Point>Sensor>Pressure Sensor>Static Pressure Sensor | Building Static Pressure Sensor | AHU | [7 empty] | Bharath
Point>Sensor>Flow Sensor>Air Flow Sensor | Bypass Air Flow Sensor | AHU | [7 empty] | Josh
Point>Sensor | CO2 Differential Sensor | AHU | [7 empty] | Bharath
Point>Setpoint>Demand Setpoint | Discharge Air Flow Demand Setpoint | AHU |  | Supply Air Flow Demand Setpoint | [5 empty] | Josh
Point>Setpoint>Reset Setpoint | Discharge Air Temperature Reset High Setpoint | AHU |  | Supply Air Temperature Reset High Setpoint | [5 empty] | Bharath
Point>Setpoint>Reset Setpoint | Discharge Air Temperature Reset Low Setpoint | AHU |  | Supply Air Temperature Reset Low Setpoint | [5 empty] | Bharath
Point>Sensor>Pressure Sensor>Static Pressure Sensor | Discharge Air Static Pressure Sensor | AHU |  | Supply Air Static Pressure Sensor
Point>Sensor>Temperature Sensor>Differential Temperature Sensor | Low Outside Air Temperature Enable Differential Sensor | AHU | [7 empty] | Bharath
Point>Setpoint>Temperature Setpoint>Discharge Air Temperature Setpoint | Min Discharge Air Temperature Setpoint | AHU | [7 empty] | Bharath
Point>Sensor>Damper Position Sensor | Mixed Air Damper Position Sensor | AHU |  | Bypass Damper Position Sensor | [5 empty] | Jason
Point>Sensor | Trace Heat Sensor | AHU
Point>Sensor>Temperature Sensor | Mixed Air Temperature Sensor | AHU | [7 empty] | Jason
Point>Sensor>CO2 Sensor | Outside Air CO2 Sensor | AHU
Point>Sensor>Damper Position Sensor | Outside Air Damper Position Sensor | AHU | [7 empty] | Jason
Point>Sensor>Dewpoint Sensor | Outside Air Dewpoint Sensor | AHU
Point>Sensor>Enthalpy Sensor | Outside Air Enthalpy Sensor | AHU
Point>Sensor>Flow Sensor>Air Flow Sensor | Outside Air Flow Sensor | AHU | [7 empty] | Jason
Point>Sensor>Humidity Sensor | Outside Air Humidity Sensor | AHU
Point>Sensor>Temperature Sensor>Differential Temperature Sensor | Outside Air Lockout Temperature Differential Sensor | AHU |  |  | Difference between measured temperature and lockout setpoint |  |  |  |  | Bharath
Point>Sensor>Temperature Sensor | Outside Air Temperature Sensor | AHU
Point>Sensor>Temperature Sensor | Return Air Temperature Sensor | AHU | [7 empty] | Jason
Point>Sensor>Temperature Sensor | Underfloor Temperature Sensor | AHU | [7 empty] | Bharath
Point>Sensor | Frost Sensor | AHU
Point>Sensor>Speed Sensor>Differential Speed Sensor | Return Fan Differential Speed Sensor | AHU
Point>Sensor>Pressure Sensor>Differential Pressure Sensor | Heat Wheel Differential Pressure Sensor | AHU | [7 empty] | Josh
Point>Sensor>Speed Sensor>Differential Speed Sensor | Heat Wheel Speed Sensor | AHU | [7 empty] | Josh
Point>Sensor>Temperature Sensor>Discharge Air Temperature Sensor | Heat Wheel Discharge Air Temperature Sensor | AHU |  | Heat Wheel Supply Air Temperature Sensor | [5 empty] | Josh
Point>Sensor>Voltage Sensor | Heat Wheel Voltage Sensor | AHU | [7 empty] | Josh
Point>Sensor>Flow Sensor>Air Flow Sensor>Fan Air Flow Sensor | Supply Fan Air Flow Sensor | AHU | [7 empty] | Bharath
Point>Sensor>Piezoelectric Sensor | Supply Fan Piezoelectric Sensor | AHU
Point>Sensor>Temperature Sensor | CRAC Temperature Sensor | CRAC | [7 empty] | Jason
Point>Sensor | Humidity Sensor | CRAC | [7 empty] | Bharath
Point>Sensor>Pressure Sensor>Differential Pressure Sensor | Chilled Water Differential Pressure Sensor | CWS | [7 empty] | Jason
Point>Sensor>Temperature Sensor>Supply Water Temperature Sensor | Chilled Water Supply Temperature Sensor | CWS | [7 empty] | Jason
Point>Sensor>Temperature Sensor>Return Water Temperature Sensor | Chilled Water Return Temperature Sensor | CWS | [5 empty] | O | X | Jason
Point>Sensor>Flow Sensor>Water Flow Sensor>Supply Water Flow Sensor | Chilled Water Supply Flow Sensor | CWS | [7 empty] | Bharath
Point>Sensor>Temperature Sensor>Differential Temperature Sensor | Chilled Water Temperature Differential Sensor | CWS |  |  | Difference between supply and return temperature |  |  |  |  | Bharath
Point>Sensor>Pressure Sensor>Differential Pressure Sensor | Chilled Water Differential Pressure Sensor | CWS | [7 empty] | Bharath
Point>Sensor>Flow Sensor>Air Flow Sensor | Exhaust Air Flow Sensor | Exhaust System | [7 empty] | Jason
Point>Sensor>Flow Sensor>Air Flow Sensor>Exhaust Air Flow Sensor | Exhaust Air Stack Flow Sensor | Exhaust System | [7 empty] | Bharath
Point>Sensor>Temperature Sensor | Exhaust Air Temperature Sensor | Exhaust System | [7 empty] | Jason
Point>Sensor>Pressure Sensor>Velocity Pressure Sensor | Exhaust Air Velocity Pressure Sensor | Exhaust System | [7 empty] | Bharath
Point>Sensor>Piezoelectric Sensor | Exhaust Fan Piezoelectric Sensor | Exhaust System | [7 empty] | Josh
Point>Sensor>Pressure Sensor>Static Pressure Sensor>Exhaust Air Static Pressure Sensor | Average Exhaust Air Static Pressure Sensor | Exhaust System | [7 empty] | Bharath
Point>Sensor>Pressure Sensor>Static Pressure Sensor | Exhaust Air Static Pressure Sensor | Exhaust System | [7 empty] | Bharath
Point>Sensor>Pressure Sensor>Static Pressure Sensor>Exhaust Air Static Pressure Sensor | Lowest Exhaust Air Static Pressure Sensor | Exhaust System | [7 empty] | Bharath
Point>Sensor>Flow Sensor>Air Flow Sensor | Fan Air Flow Sensor | Fan | [7 empty] | Jason
Point>Sensor>Pressure Sensor>Differential Pressure Sensor | Filter Differential Pressure Sensor | Filter | [7 empty] | Bharath
Point>Sensor>Temperature Sensor>Supply Water Temperature Sensor | Heat Exchanger Supply Water Temperature Sensor | HWS | [7 empty] | Bharath
Point>Sensor>Temperature Sensor>Return Water Temperature Sensor>Hot Water Return Temperature Sensor | High Temperature Hot Water Return Temperature Sensor | HWS
Point>Sensor>Temperature Sensor>Supply Water Temperature Sensor>Hot Water Supply Temperature Sensor | High Temperature Hot Water Supply Temperature Sensor | HWS
Point>Sensor>Pressure Sensor>Differential Pressure Sensor | Hot Water Differential Pressure Sensor | HWS | [7 empty] | Jason
Point>Sensor>Temperature Sensor>Supply Water Temperature Sensor | Hot Water Supply Temperature Sensor | HWS | [7 empty] | Jason
Point>Sensor>Temperature Sensor>Return Water Temperature Sensor | Hot Water Return Temperature Sensor | HWS | [7 empty] | Jason
Point>Sensor>Temperature Sensor>Return Water Temperature Sensor>Hot Water Return Temperature Sensor | Medium Temperature Hot Water Return Temperature Sensor | HWS | [7 empty] | Jason
Point>Sensor>Temperature Sensor>Supply Water Temperature Sensor>Hot Water Supply Temperature Sensor | Medium Temperature Hot Water Supply Temperature Sensor | HWS | [7 empty] | Jason
Point>Sensor>Pressure Sensor>Differential Pressure Sensor>Hot Water Differential Pressure Sensor | Medium Temperature Hot Water Differential Pressure Sensor | HWS
Point>Sensor>Temperature Sensor>Room Temperature Sensor | Cold Box Temperature Sensor | Laboratory | [7 empty] | Bharath
Point>Sensor>Temperature Sensor>Room Temperature Sensor | Environment Box Temperature Sensor | Laboratory | [7 empty] | Bharath
Point>Sensor>Temperature Sensor>Room Temperature Sensor | Freezer Temperature Sensor | Laboratory | [7 empty] | Bharath
Point>Sensor>Temperature Sensor>Room Temperature Sensor | Hot Box Temperature Sensor | Laboratory | [7 empty] | Bharath
Point>Sensor>Flow Sensor>Air Flow Sensor>Fan Air Flow Sensor | Booster Fan Air Flow Sensor | VAV
Point>Sensor | Damper Position Sensor | VAV | [5 empty] | O | X | Jason
Point>Sensor>Flow Sensor>Air Flow Sensor | Discharge Air Flow Sensor | VAV |  | Supply Air Flow Sensor | Discharge Air Flow Sensor
Point>Sensor>Pressure Sensor>Velocity Pressure Sensor | Discharge Air Velocity Pressure Sensor | VAV |  | Supply Air Velocity Pressure Sensor | [5 empty] | Bharath
Point>Sensor>Temperature Sensor | Room Temperature Sensor | VAV |  |  | Room Temperature Sensor
Point>Sensor>Temperature Sensor | Zone Temperature Sensor | VAV |  |  | Temperature sensor in the thermostat to measure the actual zone temperature
Point>Sensor | CO2 Sensor | VAV |  | CO2 Level Sensor |  |  |  | O | X | Jason
Point>Sensor>Temperature Sensor | Discharge Air Temperature Sensor | VAV |  | Supply Air Temperature Sensor
Point>Sensor | Occupancy Sensor | VAV | [5 empty] | O | X | Jason
Point>Sensor | Thermostat Adjust Sensor | VAV |  | Warm Cool Adjust Sensor | User's delta command to control temperature setpoint in thermostat |  |  | O | X | Jason
Point>Sensor>Voltage Sensor | DC Bus Voltage Sensor | VFD |  |  | Voltage measured on the communication/control lines |  |  | O | X | Bharath
Point>Sensor>Temperature Sensor | Drive Temperature Sensor | VFD |  |  | Measures VFD temperature |  |  | O | X | Bharath
Point>Sensor | Energy Sensor | VFD | [5 empty] | O | X | Bharath
Point>Sensor>Current Sensor | Motor Current Sensor | VFD |  | Load Current Sensor | Measured current |  |  | O | X | Bharath
Point>Meter>Power Meter | Motor Power Meter | VFD | [7 empty] | Bharath
Point>Sensor>Speed Sensor | Motor Speed Sensor | VFD | [7 empty] | Jason
Point>Sensor>Torque Sensor | Motor Torque Sensor | VFD |  |  | Measured torque |  |  | O | X | Bharath
Point>Sensor>Frequency Sensor | Output Frequency Sensor | VFD | [7 empty] | Bharath
Point>Sensor>Voltage Sensor | Output Voltage Sensor | VFD | [7 empty] | Bharath
Point>Sensor | Run Time Sensor | VFD |  | Running Hour Sensor
Point>Sensor | Luminance Sensor | Lighting System
Point>Sensor>Conductivity Sensor | Deionised Water Conductivity Sensor | Water System | [7 empty] | Bharath
Point>Sensor>Temperature Sensor | Water Supply Temperature Sensor | Water System | [7 empty] | Jason
Point>Sensor>Water Level Sensor | Deionised Water Level Sensor | Water System |  | DI Water Level Sensor | [5 empty] | Bharath
Point>Sensor>Temperature Sensor>Supply Water Temperature Sensor>Hot Water Supply Temperature Sensor | Domestic Hot Water Supply Temperature Sensor | DomesticHWS | [7 empty] | Bharath
Point>Sensor>Enthalpy Sensor | Outside Enthalpy Sensor | Weather | [7 empty] | Bharath
Point>Sensor>Humidity Sensor | Relative Humidity Sensor | Weather | [7 empty] | Bharath
Point>Sensor | Solar Radiance Sensor | Weather | [7 empty] | Jason
Point>Sensor>Direction Sensor | Wind Direction Sensor | Weather | [7 empty] | Jason
Point>Sensor>Speed Sensor | Wind Speed Sensor | Weather | [7 empty] | Jason
Point>Sensor | Hail Sensor | Weather
Point>Sensor | Rain Sensor | Weather
Point>Sensor | Rain Duration Sensor | Weather
Point>Sensor | Temperature Sensor |  |  |  | A general purpose temperature sensor |  |  |  |  | Aslak
Point>Sensor | Pressure Sensor |  |  |  | A general purpose pressure sensor |  |  |  |  | Aslak
Point>Sensor | Flow Sensor |  |  |  | A general purpose flow sensor |  |  |  |  | Aslak
Point>Sensor>Motion Sensor | PIR Sensor
Point>Setpoint>Pressure Setpoint>Differential Pressure Setpoint>Load Shed Differential Pressure Setpoint | Chilled Water Differential Pressure Load Shed Setpoint | Demand Response | [7 empty] | Bharath
Point>Setpoint>Pressure Setpoint>Differential Pressure Setpoint>Load Shed Differential Pressure Setpoint | Medium Temperature Hot Water Differential Pressure Load Shed Setpoint | Demand Response | [7 empty] | Bharath
Point>Setpoint>Temperature Setpoint>Supply Water Temperature Setpoint>Load Shed Supply Water Temperature Setpoint | Medium Temperature Hot Water Supply Temperature Load Shed Setpoint | Demand Response | [7 empty] | Bharath
Point>Setpoint>Temeperature Setpoint>Cooling Temperature Setpoint | AHU Auto Cooling Temperature Setpoint | AHU | [7 empty] | Josh
Point>Setpoint>Temeperature Setpoint>Cooling Temperature Setpoint | AHU Current Cooling Setpoint | AHU | [7 empty] | Josh
Point>Setpoint>Pressure Setpoint>Static Pressure Setpoint | Building Static Pressure Setpoint | AHU
Point>Setpoint>Dead Band Setpoint>Discharge Air Temperature Dead Band Setpoint | Cooling Discharge Air Temperature Dead Band Setpoint | AHU |  | Cooling Supply Air Temperature Dead Band Setpoint | [5 empty] | Bharath
Point>Setpoint>Integral Time Setpoint>Discharge Air Temperature Integral Time Setpoint | Cooling Discharge Air Temperature Integral Time Setpoint | AHU |  | Cooling Supply Air Temperature Integral Time Setpoint | [5 empty] | Bharath
Point>Setpoint>Proportional Band Setpoint>Discharge Air Temperature Proportional Band Setpoint | Cooling Discharge Air Temperature Proportional Band Setpoint | AHU |  | Cooling Supply Air Temperature Proportional Band Setpoint | [5 empty] | Bharath
Point>Setpoint>Demand Setpoint | Cooling Demand Setpoint | AHU |  | Cooling Request Percent Setpoint | [5 empty] | Josh
Point>Setpoint>Dead Band Setpoint>Static Pressure Dead Band Setpoint | Discharge Air Static Pressure Dead Band Setpoint | AHU |  | Supply Air Static Pressure Dead Band Setpoint | [5 empty] | Bharath
Point>Setpoint>Increase Decrease Step Setpoint | Discharge Air Static Pressure Increase Decrease Step Setpoint | AHU |  | Supply Air Static Pressure Increase Decrease Step Setpoint | [5 empty] | Bharath
Point>Setpoint>Integral Time Setpoint | Discharge Air Static Pressure Integral Time Setpoint | AHU |  | Supply Air Static Pressure Integral Time Setpoint | [5 empty] | Bharath
Point>Setpoint>Proportional Band Setpoint | Discharge Air Static Pressure Proportional Band Setpoint | AHU |  | Supply Air Static Pressure Proportional Band Setpoint | [5 empty] | Bharath
Point>Setpoint>Pressure Setpoint>Static Pressure Setpoint | Discharge Air Static Pressure Setpoint | AHU |  | Supply Air Static Pressure Setpoint | [5 empty] | Bharath
Point>Setpoint>Reset Setpoint>Temperature Differential Reset Setpoint | Discharge Air Temperature Reset Differential Setpoint | AHU |  | Supply Air Temperature Reset Differential Setpoint | [5 empty] | Bharath
Point>Setpoint>Temperature Setpoint | Discharge Air Temperature Setpoint | AHU |  | Supply Air Temperature Setpoint | [5 empty] | Jason
Point>Setpoint>Increase Decrease Step Setpoint | Discharge Air Temperature Setpoint Increase Decrease Step | AHU |  | Supply Air Temperature Setpoint Increase Decrease Step | [5 empty] | Bharath
Point>Setpoint>Mode Setpoint | DualBand Mode Setpoint | AHU |  |  | virtual point used for controls |  |  |  |  | Marco
Point>Setpoint>Temperature Setpoint>Discharge Air Temperature Setpoint | Economizer Differential Air Temperature Setpoint | AHU |  |  | Difference between return air flow and outside air flow |  |  |  |  | Bharath
Point>Setpoint>Dead Band Setpoint>Discharge Air Temperature Dead Band Setpoint | Economizer Discharge Air Temperature Dead Band Setpoint | AHU | [7 empty] | Bharath
Point>Setpoint>Proportional Band Setpoint>Discharge Air Temperature Proportional Band Setpoint | Economizer Discharge Air Temperature Proportional Band Setpoint | AHU | [7 empty] | Bharath
Point>Setpoint>Flow Setpoint>Air Flow Setpoint | Economizer Outside Air Flow Setpoint | AHU | [7 empty] | Bharath
Point>Setpoint>Demand Setpoint | Heating Demand Setpoint | AHU |  | Heat Request Percent Setpoint | [5 empty] | Josh
Point>Setpoint>Dead Band Setpoint>Discharge Air Temperature Dead Band Setpoint | Heating Discharge Air Temperature Dead Band Setpoint | AHU | [7 empty] | Bharath
Point>Setpoint>Integral Time Setpoint>Discharge Air Temperature Integral Time Setpoint | Heating Discharge Air Temperature Integral Time Setpoint | AHU | [7 empty] | Bharath
Point>Setpoint>Proportional Band Setpoint>Discharge Air Temperature Proportional Band Setpoint | Heating Discharge Air Temperature Proportional Band Setpoint | AHU | [7 empty] | Bharath
Point>Setpoint>Temperature Setpoint | Low Outside Air Temperature Enable Setpoint | AHU |  |  | Temperature at which outside air is "Low" |  |  |  |  | Bharath
Point>Setpoint>Pressure Setpoint>Static Pressure Setpoint>Discharge Air Static Pressure Setpoint | Max Discharge Air Static Pressure Setpoint | AHU | [7 empty] | Bharath
Point>Setpoint>Temperature Setpoint>Discharge Air Temperature Setpoint | Max Discharge Air Temperature Setpoint | AHU | [7 empty] | Bharath
Point>Setpoint>CO2 Setpoint>Return Air CO2 Setpoint | Max Return Air CO2 Setpoint | AHU | [7 empty] | Josh
Point>Setpoint>Speed Setpoint>VFD Speed Setpoint | Max VFD Speed Setpoint | AHU |  |  | Max VFD Speed To Increase Static Pressure Setpoint |  |  |  |  | Bharath
Point>Setpoint>Pressure Setpoint>Static Pressure Setpoint>Discharge Air Static Pressure Setpoint | Min Discharge Air Static Pressure Setpoint | AHU | [7 empty] | Bharath
Point>Setpoint>Speed Setpoint>VFD Speed Setpoint | Min VFD Speed Setpoint | AHU |  |  | Min VFD Speed To Increase Static Pressure Setpoint |  |  |  |  | Bharath
Point>Setpoint>Temperature Setpoint | Mixed Air Temperature Setpoint | AHU | [7 empty] | Marco
Point>Setpoint>Damper Position Setpoint>Outside Air Damper Position Setpoint | Outside Air Damper Min Position Setpoint | AHU |  | Economizer Damper Min Position Setpoint | Part of economizer to ensure minimum air flow |  |  |  |  | Bharath
Point>Setpoint>Temperature Setpoint | Outside Air Lockout Temperature Setpoint | AHU |  |  | Temperature at which chiller stops cooling because outside air is too cold already |  |  |  |  | Bharath
Point>Setpoint>Reset Setpoint>Temperature High Reset Setpoint | Outside Air Temperature High Reset Setpoint | AHU | [7 empty] | Bharath
Point>Setpoint>Reset Setpoint>Temperature Low Reset Setpoint | Outside Air Temperature Low Reset Setpoint | AHU | [7 empty] | Bharath
Point>Setpoint>Flow Setpoint>Air Flow Setpoint | Outside Min Air Flow Setpoint | AHU | [7 empty] | Jason
Point>Setpoint>Demand Setpoint | Preheat Demand Setpoint | AHU | [7 empty] | Josh
Point>Setpoint>Speed Setpoint>Differential Speed Setpoint | Return Supply Fan Differential Speed Setpoint | AHU |  | Return Fan Differential Speed Setpoint | [5 empty] | Bharath
Point>Setpoint>Pressure Setpoint>Static Pressure Setpoint | Static Pressure Max Setpoint | AHU |  |  | Max Static Pressure in the supply duct (per Design) |  |  |  |  | Marco
Point>Setpoint>Pressure Setpoint>Static Pressure Setpoint | Static Pressure Min Setpoint | AHU | [7 empty] | Bharath
Point>Setpoint>Mode Setpoint | Unoccupied Mode Setpoint | AHU |  |  | virtual point used for controls |  |  |  |  | Marco
Point>Setpoint>Demand Setpoint | VAV Cooling Demand Setpoint | AHU |  | VAV Cooling Request Setpoint | [5 empty] | Josh
Point>Setpoint>Demand Setpoint | VAV Heating Demand Setpoint | AHU |  | VAV Heat Request Setpoint | [5 empty] | Josh
Point>Setpoint>Dead Band Setpoint | Chilled Water Differential Pressure Dead Band Setpoint | CWS
Point>Setpoint>Increase Decrease Step Setpoint | Chilled Water Differential Pressure Increase Decrease Step Setpoint | CWS | [7 empty] | Bharath
Point>Setpoint>Integral Time Setpoint | Chilled Water Differential Pressure Integral Time Setpoint | CWS
Point>Setpoint>Proportional Band Setpoint | Chilled Water Differential Pressure Proportional Band Setpoint | CWS
Point>Setpoint>Pressure Setpoint>Differential Pressure Setpoint | Chilled Water Differential Pressure Setpoint | CWS | [5 empty] | O | X | Jason
Point>Setpoint>Pressure Setpoint>Static Pressure Setpoint | Chilled Water Static Pressure Setpoint | CWS | [7 empty] | Jason
Point>Setpoint>Pressure Setpoint>Differential Pressure Setpoint>Chilled Water Differential Pressure Setpoint | Max Chilled Water Differential Pressure Setpoint | CWS | [7 empty] | Bharath
Point>Setpoint>Pressure Setpoint>Differential Pressure Setpoint>Chilled Water Differential Pressure Setpoint | Min Chilled Water Differential Pressure Setpoint | CWS | [7 empty] | Bharath
Point>Setpoint>Alarm Delay Setpoint>Pump Alarm Delay Setpoint | Chilled Water Pump Alarm Delay Setpoint | CWS | [7 empty] | Jason
Point>Setpoint>Dead Band Setpoint>Differential Pressure Dead Band Setpoint | Chilled Water Pump Differential Pressure Dead Band Setpoint | CWS | [7 empty] | Bharath
Point>Setpoint>Integral Time>Differential Pressure Integral Time | Chilled Water Pump Differential Pressure Integration Time Setpoint | CWS | [7 empty] | Bharath
Point>Setpoint>Proportional Band>Differential Pressure Proportional Band | Chilled Water Pump Differential Pressure Proportional Band Setpoint | CWS | [7 empty] | Bharath
Point>Setpoint>Dead Band Setpoint>Exhaust Air Flow Dead Band Setpoint | Exhaust Air Stack Flow Dead Band Setpoint | Exhaust System | [7 empty] | Bharath
Point>Setpoint>Integral Time Setpoint>Exhaust Air Flow Integral Time Setpoint | Exhaust Air Stack Flow Integral Time Setpoint | Exhaust System | [7 empty] | Bharath
Point>Setpoint>Proportional Band Setpoint>Exhaust Air Flow Proportional Band Setpoint | Exhaust Air Stack Flow Proportional Band Setpoint | Exhaust System | [7 empty] | Bharath
Point>Setpoint>Flow Setpoint>Air Flow Setpoint>Exhaust Air Flow Setpoint | Exhaust Air Stack Flow Setpoint | Exhaust System | [7 empty] | Bharath
Point>Setpoint>Dead Band Setpoint>Static Pressure Dead Band Setpoint | Exhaust Air Static Pressure Dead Band Setpoint | Exhaust System | [7 empty] | Bharath
Point>Setpoint>Integral Time Setpoint>Static Pressure Integral Time Setpoint | Exhaust Air Static Pressure Integral Time Setpoint | Exhaust System | [7 empty] | Bharath
Point>Setpoint>Proportional Band Setpoint>Static Pressure Proportional Band Setpoint | Exhaust Air Static Pressure Proportional Band Setpoint | Exhaust System | [7 empty] | Bharath
Point>Setpoint>Pressure Setpoint>Static Pressure Setpoint | Exhaust Air Static Pressure Setpoint | Exhaust System | [7 empty] | Bharath
Point>Setpoint>Flow Setpoint>Air Flow Setpoint | Exhaust Fan Air Flow Setpoint | Exhaust System | [7 empty] | Josh
Point>Setpoint>Temperature Setpoint | Enable Hot Water System Outside Air Temperature Setpoint | HWS
Point>Setpoint>Dead Band Setpoint>Differential Pressure Dead Band Setpoint | Hot Water Differential Pressure Dead Band Setpoint | HWS
Point>Setpoint>Integral Time Setpoint>Differential Pressure Integral Time Setpoint | Hot Water Differential Pressure Integral Time Setpoint | HWS
Point>Setpoint>Proportional Band Setpoint>Differential Pressure Proportional Band Setpoint | Hot Water Differential Pressure Proportional Band Setpoint | HWS
Point>Setpoint>Pressure Setpoint>Differential Pressure Setpoint | Hot Water Differential Pressure Setpoint | HWS | [7 empty] | Jason
Point>Setpoint>Pressure Setpoint>Static Pressure Setpoint | Hot Water Static Pressure Setpoint | HWS | [7 empty] | Jason
Point>Setpoint>Reset Setpoint>Temperature High Reset Setpoint>Hot Water Supply Temperature High Reset Setpoint | Medium Temperature Hot Water Supply Temperature High Reset Setpoint | HWS | [7 empty] | Jason
Point>Setpoint>Reset Setpoint>Temperature Low Reset Setpoint>Hot Water Supply Temperature Low Reset Setpoint | Medium Temperature Hot Water Supply Temperature Low Reset Setpoint | HWS | [7 empty] | Jason
Point>Setpoint>Temperature Setpoint | Open Heating Valve Outside Air Temperature Setpoint | HWS | [7 empty] | Bharath
Point>Setpoint>Temperature Setpoint | Disable Hot Water System Outside Air Temperature Setpoint | HWS | [7 empty] | Bharath
Point>Setpoint>Dead Band Setpoint>Supply Water Temperature Dead Band Setpoint | Heat Exchanger Supply Water Temperature Dead Band Setpoint | HWS | [7 empty] | Bharath
Point>Setpoint>Integral Time Setpoint>Supply Water Temperature Integral Time Setpoint | Heat Exchanger Supply Water Temperature Integral Time Setpoint | HWS | [7 empty] | Bharath
Point>Setpoint>Proportional Band Setpoint>Supply Water Temperature Proportional Band Setpoint | Heat Exchanger Supply Water Temperature Proportional Band Setpoint | HWS | [7 empty] | Bharath
Point>Setpoint>Temperature Setpoint>Supply Water Temperature Setpoint | Heat Exchanger Supply Water Temperature Setpoint | HWS | [7 empty] | Bharath
Point>Setpoint>Flow Setpoint>Air Flow Setpoint>Discharge Air Flow Setpoint>Cooling Discharge Air Flow Setpoint | Cooling Max Discharge Air Flow Setpoint | VAV |  | Cooling Max Supply Air Flow Setpoint |  |  |  | O | X | Jason
Point>Setpoint>Flow Setpoint>Air Flow Setpoint>Discharge Air Flow Setpoint>Cooling Discharge Air Flow Setpoint | Cooling Min Discharge Air Flow Setpoint | VAV |  | Cooling Min Supply Air Flow Setpoint
Point>Setpoint>Flow Setpoint>Air Flow Setpoint | Discharge Air Flow Setpoint | VAV |  | Supply Air Flow Setpoint |  |  |  | O | X | Jason
Point Setpoint>Temperature Setpoint>Zone Temperature Setpoint | Zone Cooling Temperature Setpoint |  |  | Zone Temperature High Setpoint
Point Setpoint>Temperature Setpoint>Zone Temperature Setpoint | Zone Heating Temperature Setpoint |  |  | Zone Temperature Low Setpoint
Point>Setpoint>Temperature Setpoint>Zone Temperature Setpoint>Zone Cooling Temperature Setpoint | Effective Cooling Temperature Setpoint | VAV | [7 empty] | Bharath
Point>Setpoint>Temperature Setpoint>Zone Temperature Setpoint>Zone Heating Temperature Setpoint | Effective Heating Temperature Setpoint | VAV | [7 empty] | Bharath
Point>Setpoint>Flow Setpoint>Air Flow Setpoint>Discharge Air Flow Setpoint | Heating Discharge Air Flow Setpoint | VAV | [7 empty] | Jason
Point>Setpoint>Flow Setpoint>Air Flow Setpoint>Discharge Air Flow Setpoint>Heating Discharge Air Flow Setpoint | Heating Max Discharge Air Flow Setpoint | VAV
Point>Setpoint>Flow Setpoint>Air Flow Setpoint>Discharge Air Flow Setpoint>Heating Discharge Air Flow Setpoint | Heating Min Discharge Air Flow Setpoint | VAV
Point>Setpoint>Flow Setpoint>Air Flow Setpoint>Discharge Air Flow Setpoint>Cooling Discharge Air Flow Setpoint | Occupied Cooling Discharge Air Flow Setpoint | VAV | [7 empty] | Bharath
Point>Setpoint>Flow Setpoint>Air Flow Setpoint>Discharge Air Flow Setpoint>Cooling Discharge Air Flow Setpoint>Occupied Cooling Discharge Air Flow Setpoint | Occupied Cooling Max Discharge Air Flow Setpoint | VAV | [7 empty] | Bharath
Point>Setpoint>Flow Setpoint>Air Flow Setpoint>Discharge Air Flow Setpoint>Cooling Discharge Air Flow Setpoint>Occupied Cooling Discharge Air Flow Setpoint | Occupied Cooling Min Discharge Air Flow Setpoint | VAV |  | Occupied Cooling Min Supply Air Flow Setpoint |  |  |  | O | X | Jason
Point>Setpoint>Dead Band Setpoint>Zone Cooling Temperature Dead Band Setpoint | Occupied Cooling Temperature Dead Band Setpoint | VAV
Point>Setpoint>Flow Setpoint>Air Flow Setpoint>Discharge Air Flow Setpoint>Heating Discharge Air Flow Setpoint | Occupied Heating Discharge Air Flow Setpoint | VAV |  | Occupied Heating Supply Air Flow Setpoint |  |  |  | O | X | Jason
Point>Setpoint>Flow Setpoint>Air Flow Setpoint>Discharge Air Flow Setpoint>Heating Discharge Air Flow Setpoint>Occupied Heating Discharge Air Flow Setpoint | Occupied Heating Max Discharge Air Flow Setpoint | VAV | [7 empty] | Bharath
Point>Setpoint>Flow Setpoint>Air Flow Setpoint>Discharge Air Flow Setpoint>Heating Discharge Air Flow Setpoint>Occupied Heating Discharge Air Flow Setpoint | Occupied Heating Min Discharge Air Flow Setpoint | VAV | [7 empty] | Bharath
Point>Setpoint>Dead Band Setpoint>Zone Heating Temperature Dead Band Setpoint | Occupied Heating Temperature Dead Band Setpoint | VAV
Point>Setpoint>Temperature Setpoint | Room Temperature Setpoint | VAV |  |  |  | Fahrenheit
Point>Setpoint>Temperature Setpoint | Schedule Temperature Setpoint | VAV | [7 empty] | Josh
Point>Setpoint>Flow Setpoint>Air Flow Setpoint>Discharge Air Flow Setpoint>Cooling Discharge Air Flow Setpoint | Unoccupied Cooling Discharge Air Flow Setpoint | VAV
Point>Setpoint>Temperature Setpoint>Zone Temperature Setpoint>Zone Cooling Temperature Setpoint | Unoccupied Cooling Temperature Setpoint | VAV | [7 empty] | Bharath
Point>Setpoint>Temperature Setpoint>Zone Temperature Setpoint>Zone Heating Temperature Setpoint | Unoccupied Heating Temperature Setpoint | VAV | [7 empty] | Bharath
Point>Setpoint | Zone Temperature Setpoint | VAV |  |  | A temperature setpoint in charge of a zone. | Fahrenheit |  | O | X | Jason
Point>Setpoint | Acceleration Time Setpoint | VFD |  |  | Setpoint for acceleration |  |  | O | X | Bharath
Point>Setpoint | Current Limit Setpoint | VFD |  |  | Setpoint for max current consumed by VFD |  |  | O | X | Bharath
Point>Setpoint | Deceleration Time Setpoint | VFD |  |  | Setpoint for deceleration |  |  | O | X | Bharath
Point>Setpoint | Rated Speed Setpoint | VFD |  |  | Maximum speed specified by manufacturer |  |  | O | X | Bharath
Point>Setpoint>Dead Band Setpoint>Supply Water Differential Pressure Dead Band Setpoint | Thermal Energy Storage Supply Water Differential Pressure Dead Band Setpoint | Thermal Energy Storage | [7 empty] | Bharath
Point>Setpoint>Integral Time Setpoint>Supply Water Differential Pressure Integral Time Setpoint | Thermal Energy Storage Supply Water Differential Pressure Integral Time Setpoint | Thermal Energy Storage | [7 empty] | Bharath
Point>Setpoint>Proportional Band Setpoint>Supply Water Differential Pressure Proportional Band Setpoint | Thermal Energy Storage Supply Water Differential Pressure Proportional Band Setpoint | Thermal Energy Storage | [7 empty] | Bharath
Point>Setpoint>Speed Setpoint>Fan Speed Setpoint | Cooling Tower Fan Speed Setpoint | Water System | [5 empty] | O | X | Jason
Point>Setpoint>Temperature Setpoint | Supply Water Temperature Setpoint | Water System | [7 empty] | Bharath
Point>Setpoint>Temeprature Setpoint>Supply Water Temperature Setpoint>Hot Water Supply Temperature Setpoint | Domestic Hot Water Supply Temperature Setpoint | DomesticHWS | [7 empty] | Bharath
Point>Setpoint>Alarm Delay Setpoint | Pump Alarm Delay Setpoint | Pump
Point>Status | Turn Off Status | [8 empty] | Jason
Point>Status>Load Shed Status>Differential Pressure Load Shed Status | Chilled Water Differential Pressure Load Shed Status | Demand Response |  | Chilled Water Differential Pressure Load Shed Reset | [5 empty] | Bharath
Point>Status | Load Shed Status | Demand Response
Point>Status>Load Shed Status>Differential Pressure Load Shed Status | Medium Temperature Hot Water Differential Pressure Load Shed Status | Demand Response |  | Medium Temperature Hot Water Differential Pressure Load Shed Reset | [5 empty] | Bharath
Point>Status>Load Shed Status>Differential Pressure Load Shed Status | Medium Temperature Hot Water Supply Temperature Load Shed Status | Demand Response | [7 empty] | Bharath
Point>Status | Emergency Generator Status | Emergency Generator | [7 empty] | Bharath
Point>Status | Emergency Air Flow Status | Fume Hood |  |  | Binary value indicating if emergency air flow is on/off |  |  |  |  | Bharath
Point>Status | Emergency Push Button Status | Fume Hood | [7 empty] | Bharath
Point>Status>Overridden Status | AHU Overridden Off Status | AHU |  |  | Indicates if the AHU has been manually overridden to be Off |  |  |  |  | Bharath
Point>Status>Overridden Status | AHU Overridden On Status | AHU |  |  | Indicates if the AHU has been manually overridden to be On |  |  |  |  | Bharath
Point>Status>Mode Status | Economizer Mode Status | AHU |  | Economizer Status | virtual point used for controls |  |  |  |  | Marco
Point>Status | Fan Run Request Status | AHU |  |  | Request from AHU for the fan to run |  |  |  |  | Bharath
Point>Status | Start Stop Status |  |  | On Off Status
Point>Status>Start Stop Status | Fan Start Stop Status | AHU | [7 empty] | Jason
Point>Status | Filter Status | AHU | [7 empty] | Bharath
Point>Status>Mode Status | Occupied Mode Status | AHU |  |  | virtual point used for controls |  |  |  |  | Marco
Point>Status>Filter Status | Pre Filter Status | AHU |  |  | Pre-filter filters large particles. Point indicates the if filter is dirty |  |  |  |  | Bharath
Point>Status>Start Stop Status | Return Fan Start Stop Status | AHU |  | Return Fan Status | [5 empty] | Bharath
Point>Status>Start Stop Status | Supply Fan Start Stop Status | AHU |  | Supply Fan Status | [5 empty] | Bharath
Point>Status | System Shutdown Status | AHU
Point>Status>On Off Status | Cooling On Off Status | CRAC | [7 empty] | Bharath
Point>Status | CRAC Stages Status | CRAC | [7 empty] | Bharath
Point>Status>On Off Status | Dehumidification On Off Status | CRAC | [7 empty] | Bharath
Point>Status>On Off Status | EconCycle On Off Status | CRAC | [7 empty] | Bharath
Point>Status>Emergency Power Off Status | Emergency Power Off Activated By High Temperature Status | CRAC | [7 empty] | Bharath
Point>Status>Emergency Power Off Status | Emergency Power Off Activated By Leak Detection System Status | CRAC | [7 empty] | Bharath
Point>Status>Emergency Power Off Status | Emergency Power Off Enable Status | CRAC | [7 empty] | Bharath
Point>Status>Emergency Power Off Status | Emergency Power Off System Enable Status | CRAC | [7 empty] | Jason
Point>Status>On Off Status | Heating On Off Status | CRAC | [7 empty] | Bharath
Point>Status>On Off Status | Humidification On Off Status | CRAC | [7 empty] | Bharath
Point>Status>Fault Status | Humidifier Fault Status | CRAC
Point>Status>Start Stop Status>Fan Start Stop Status | Standby Fan Status | CRAC | [7 empty] | Bharath
Point>Status>On Off Status | Standby Glycool Unit On Off Status | CRAC | [7 empty] | Bharath
Point>Status>On Off Status | Standby Unit On Off Status | CRAC | [7 empty] | Bharath
Point>Status | CRAC Unit Hold Status | CRAC | [7 empty] | Bharath
Point>Status>Start Stop Status | CRAC Unit Run Status | CRAC |  | CRAC Unit Start Stop Status | [5 empty] | Bharath
Point>Status>Turned Off Status | CRAC Unit Turned Off Locally Status | CRAC | [7 empty] | Bharath
Point>Status>Turned Off Status | CRAC Unit Turned Off Remotely Status | CRAC | [7 empty] | Bharath
Point>Status>Enable Status | Chilled Water Pump Enable Status | CWS |  |  | Allows the pump to be used. It is a sensor. |  |  |  |  | Bharath
Point>Status>Pump Lead Lag Status | Chilled Water Pump Lead Lag Status | CWS
Point>Status>Start Stop Status>Pump Start Stop Status | Chilled Water Pump Start Stop Status | CWS |  | Chilled Water Pump Status
Point>Status>Disable Status | Exhaust Fan Disable Status | Exhaust System | [7 empty] | Bharath
Point>Status>Overridden Status | Exhaust Fan Overridden Off Status | Exhaust System | [7 empty] | Bharath
Point>Status>Overridden Status | Exhaust Fan Overridden On Status | Exhaust System | [7 empty] | Bharath
Point>Status>Start Stop Status | Exhaust Fan Status | Exhaust System |  | Exhaust Fan Start Stop Status | [5 empty] | Bharath
Point>Status>Fire Control Panel LED Status | AHU Off Status LED | Fire Control Panel
Point>Status>Fire Control Panel LED Status | AHU On Status LED | Fire Control Panel
Point>Status>Fire Control Panel LED Status | Exhaust Fan Off Status LED | Fire Control Panel
Point>Status>Fire Control Panel LED Status | Exhaust Fan On Status LED | Fire Control Panel
Point>Status>Enable Status | Heat Exchanger System Enable Status | HWS | [7 empty] | Bharath
Point>Status>Valve Status | Heat Exchanger Valve Status | HVAC |  |  | Indicates if valve is being used or not. Important for multi-valve systems |  |  |  |  | Bharath
Point>Status>Occupancy Status | Temporary Occupancy Status | VAV |  |  | Sensor that indicates the button on thermostat has been pressed on weekend/nights. Typically turns On HVAC for a set number of hours. |  |  | O | X | Jason
Point>Status | Drive Ready Status | VFD |  |  | TBD |  |  | O | X | Bharath
Point>Status | Fault Status | VFD |  | Fault Indicator Status |  |  |  | O | X | Bharath
Point>Status | Last Fault Code Status | VFD |  |  | TBD |  |  |  |  | Bharath
Point>Status | Manual Auto Status | VFD |  | Hand Auto Status | Indicates if it is in manual or auto mode. |  |  | O | X | Bharath
Point>Status>Direction Status | Run Direction Status | VFD |  | Motor Direction Status | Status of VFD direction. Synonym |  |  | O | X | Bharath
Point>Status>Enable Status | Run Enable Status | VFD | [7 empty] | Bharath
Point>Status>Start Stop Status | VFD Start Stop Status | VFD |  | Motor Start Stop Status, VFD Run Status | [5 empty] | Bharath
Point>Status | Even Month Status | Time | [7 empty] | Bharath
Point>Status | Freeze Status | Water System | [5 empty] | O | X | Jason
Point>Status>Start Stop Status | Pump Status | Water System |  | Pump Start Stop Status
Point>Status>Enable Status | Pump Enable Status | Pump
Resource>Air | Mixed Air |  | AHU | [6 empty] | Jason
Resource>Air | Outside Air |  | AHU | [6 empty] | Jason
Resource>Air | Return Air |  | AHU | [6 empty] | Jason
Resource>Water | Chilled Water |  | CWS | [6 empty] | Jason
Resource>Water | Hot Water |  | HWS | [6 empty] | Jason
Resource>Water>Hot Water | Medium Temperature Hot Water |  | HWS | [6 empty] | Jason
Resource>Water>Hot Water | High Temperature Hot Water |  | HWS | [6 empty] | Jason
Resource>Air | Discharge Air |  | VAV
Resource>Water | Deionised Water |  | Water System | DI Water | Very pure water. Used in research labs |  |  |  |  | Bharath
Resource>Water>Hot Water | Domestic Hot Water |  | DomesticHWS | [6 empty] | Jason

## InfoDim
Note: Information dimensions describe high level concepts that are useful to group TagSets describing the same area of information such as Locations.
Tag Set | Author | Reviewed | Review Count | Comments
AssetDimension | (Add the definition of Asset here)
Air Handler Unit | Joern
Variable Air Volume | Jason
FunctionDimension | (Add the definition of Function here)
Return Air Temperature

## Triples
Possible Subject (Tag Set) | Predicate | Possible Object (Tag Set) | Definition of Predicate | Author | Reviewed | Review Count | Comments
Examples
Zone Temperature Sensor | isLocatedIn | Room | Object indicates the location of subject. Object should be the most fine unit. | Jason
Thermostat |  | Room |  | Jason
hasUnit
Easier to populate in "Tag Sets" sheet
hasSynonym
Easier to populate in "Tag Sets" sheet
hasAbbreviation
Easier to populate in "Tag Sets" sheet
hasPoint
VAV Box | hasPoint | Zone Temperature Sensor |  |  |  |  | These can be autopopulated from tagsets sheet as they are already partially organized
Zone Temperature Setpoint
Room Temperature Setpoint
Room Temperature Sensor
Effective Heating Temperature Setpoint
Effective Cooling Temperature Setpoint
Occupied Heating Temperature Setpoint
Occupied Cooling Temperature Setpoint
Temporary Occupancy Status
Reheat Valve Command
Heating Valve Command
Discharge Air Flow Sensor
Discharge Air Flow Setpoint
Occupied Cooling Max Discharge Air Flow
Cooling Max Discharge Air Flow
Occupied Heating Max Discharge Air Flow
Occupied Heating Min Discharge Air Flow
Heating Supply Air Flow
Occupied Cooling Min Discharge Air Flow
VAV Box Mode
Heating Command
Cooling Command
Occupancy Command
Occupancy Sensor
Damper Command
Damper Position Sensor
Booster Fan Start Stop Command
Booster Fan Command
Booster Fan Air Flow Sensor
CO2 Sensor
CO2 High Alarm
AHU (not complete yet) | hasPoint | Change Filter Alarm
Pre Filter Status
Filter Status
Filter Differential Pressure Sensor
Return Air Preheat Valve Command
Preheat Supply Air Temperature
Preheat Demand
Run Request
VAV Heat Request
Heat Request Percent
VAV Cool Request
Cool Request Percent
Building Static Pressure Setpoint
Building Static Pressure Sensor
VFD | hasPoint | Output Frequency
Frequency Command
Max Frequency Command
Output Voltage
Current Limit
Last Fault Code
Fault Reset
Fault Indicator
Filter Reset
Panel Lockout Command
Rated Speed
Speed Command
Motor Speed
Run Direction Command
Run Direction Status
Run Enable
System Enable
Energy
Motor Torque
DC Bus Voltage
Acceleration Time
Deceleration Time
Manual Auto Status
Drive Temperature
VFD Start Stop Command
VFD Start Stop Status
Drive Ready Status
Motor Current
Motor Power
Cooling Valve Command
Maintenance Mode
VFD Alarm
Fan Command
Run Time
Air Flow Estimation
Chilled Water Pump | hasPoint | Chilled Water Pump Start Stop Command
Min Chilled Water Differential Pressure Setpoint
Max Chilled Water Differential Pressure Setpoint
Chilled Water Differential Pressure Sensor
Chilled Water Differential Pressure Setpoint
Chilled Water Differential Pressure Integral Time
Chilled Water Differential Pressure Dead Band
Chilled Water Differential Pressure Proportional Band
Chilled Water Differential Pressure Increase Decrease Step
Chilled Water Return Temperature
Freeze Status
Chilled Water Pressure Setpoint
Chilled Water Discharge Temperature
Chilled Water Temperature Differential
Chilled Water Supply Flow
Chilled Water Bypass Valve Command
Pump Start Stop Command
Hot Water Pump | hasPoint | Hot Water Static Pressure Setpoint
Hot Water Differential Pressure
Hot Water Differential Pressure Setpoint
Hot Water Differential Pressure Integral Time
Hot Water Differential Pressure Proportional Band
Hot Water Differential Pressure Dead Band
Hot Water Return Temperature
Hot Water Discharge Temperature
High Temperature Hot Water Return Temperature
High Temperature Hot Water Supply Temperature
Medium Temperature Hot Water
Medium Temperature Hot Water Return Temperature
Medium Temperature Hot Water Supply Temperature
Medium Temperature Hot Water Discharge Temperature High Reset Setpoint
Medium Temperature Hot Water Discharge Temperature Low Reset Setpoint
Heat Exchanger | hasPoint | Heat Exchanger Supply Water Temperature Setpoint
Heat Exchanger Supply Water Temperature
Heat Exchanger Supply Water Temperature Proportional Band
Heat Exchanger Supply Water Temperature Integral Time
Heat Exchanger Supply Water Temperature Dead Band
Heat Exchanger Valve Command
Heat Exchanger Valve Status
Heat Exchanger System Enable
VFD | hasPoint | Output Frequency
Frequency Command
Max Frequency Command
Output Voltage
Current Limit
Last Fault Code
Fault Reset
Fault Indicator
Filter Reset
Panel Lockout Command
Rated Speed
Speed Command
Motor Speed
Run Direction Command
Run Direction Status
Run Enable
System Enable
Energy
Motor Torque
DC Bus Voltage
Acceleration Time
Deceleration Time
Manual Auto Status
Drive Temperature
VFD Start Stop Command
VFD Start Stop Status
Drive Ready Status
Motor Current
Motor Power
Cooling Valve Command
Maintenance Mode
VFD Alarm
Fan Command
Run Time
Air Flow Estimation
contains
VAV Box | contains | Reheat Valve
Damper
Booster Fan
Exhaust Fan
AHU | contains | Heating Valve
Cooling Valve
Supply Fan
Return Fan
Economizer
Pump | contains | VFD
Fan | contains | VFD
HVAC Zone | contains | Room
Floor | contains | Room
HVAC Zone
feeds
AHU | feeds | VAV
Cooling Coil | feeds | AHU
Temperature Sensor | feeds | Heat Exchanger Primary Flow |  | aslak
hasProperty
Air | hasProperty | Temperature
Humidity
Static Pressure
Velocity Pressure
Differential Pressure
Flow
Water | hasProperty | Temperature
Static Pressure
Differential Pressure
Flow
ts:Temperature_Setpoint | subClassOf | ts:FunctionTagSet;
ts:FunctionTagSet | hasDimension | FunctionDimension |  | Joern
"Schedule5" | controls | "Temperature Setpoint"
"Zone Temperature Sensor 405" | isInputOf | "Zone 405 temperature controller"
"Zone Air Flow Sensor 405" | isOutputOf | "Zone 405 temperature controller"
Discharge Fan | actuates | Discharge Air Flow |  | Jason |  |  | (Or should it be air?, Jason)

## Classes
Level 1 (Highest) | Level 2 | Level 3 | Level 4 | Level 5 | Synonym | Definition
Equipment
HVAC Equipment
AHU
Terminal Unit
VAV
VAV Single Duct with Hot Water Reheat
Fan Coil Unit
Reheat Coil Unit
Space Heater
Thermostat
Fume Hood
Chiller
Cooling Tower
Boiler
Coil
Heat Exchanger
Reheat Coil
Cooling Coil
Fan
Supply Fan
Return Fan
Exhaust Fan
Booster Fan
Pump
Chilled Water Pump
Hot Water Pump
VFD
Damper
Outside Air Damper
Return Air Damper
Valve
Heating Valve
Cooling Valve
Thermal Energy Storage
Economizer
CRAC
Lighting Equipment
CFL Bulb
LED Bulb
Ballast Lights
Solar Panel Equipment
Weather Monitoring Equipment
Point
Sensor
Setpoint
Command
Alarm
Timer
Resource
Air
Outside Air
Mixed Air
Return Air
Discharge Air
Exhaust Air
Water
Chilled Water
Chilled Water Supply
Chilled Water Return
Hot Water
Medium Temperature Hot Water
|  |  |  | Medium Temperature Hot Water Supply | Hot Water Supply
|  |  |  | Medium Temperature Hot Water Return | Hot Water Return
High Temperature Hot Water
High Temperature Hot Water Supply
High Temperature Hot Water Return
Domestic Hot Water
Deionized Water
Energy
Electrical Energy
Thermal Energy
Location
Building
Floor
Room
HVAC Zone

## Predicates
Defines the predicates, i.e., relationships we are interested in
Predicate | Reverse Predicate
Properties
hasUnit
hasDataType
hasSynonym
hasAbbreviation
measures | isMeasuredBy | Measures property | do not use! Use "hasPoint"
Connection between Equipment
hasInput | isInputOf
hasOutput | isOutputOf
feeds | isFedBy |  | Connects physical infrastructure through pipes, ducts, etc: how equipment is connected together
isPartOf | hasPart |  | Associates some subcomponent with a larger piece. Can be used for one equipment (e.g. VFD) is part of another equipment (VAV)
controls | isControlledBy
isPointOf | hasPoint | Connects point to equipment or to other entities (e.g. a room may "hasPoint" temperature sensor)
isLocatedIn | contains | Physical encapsulation: something is physically within something else, e.g. room in a floor, floor in a building, room in an hvac zone